Was nice talking to you. Sooo this is my mess. Ge model 90-30 with a cutler hammer touch screen that’s dead. I would like to install new recommended plc and a new touch screen so I can view the program. The last picture( 0460) I would like to add a test online function.  As of now we have to open the air switch to test monthly. There is no syncing on this switchgear it all works kind of  like a transfer switch. Main opens , all breakers open, generator starts then the gen breaker closes followed by the the other breakers. So when you get a chance let me know when we can schedule. Thank you.

Scott Averill
Electrician III, CCC
530-257-2181, X4766
Scott.averill@cdcr.ca.gov

# Questions
Sent to Gary 11Dec2019

Explain the operation of Circuit Breaker Switches, CS-U and CS-G. They are 3 Position, but have 4 states. What does “not” and “noc” mean?

Looking at the Inputs for the existing GE PLC on Drawing Number E1554P-15 & -17

The first 7 Inputs come from the PCRM. What does PCRM stand for?
What is a ECM Fault?

The next 5 Inputs come from RBA1. What is RBA1?

27U is an under voltage relay at the Substation Entry.
- What does the Contact being open signify?
- What does the Contact being closed signify?

UFM is not listed in the Abbreviations Legend on the first sheet.
- What does the Contact being open signify?
- What does the Contact being closed signify?

VFR (Voltage Frequency Relay) is from the Generator, but is not listed in the Abbreviations Legend on the first sheet.
- What does the Contact being open signify?
- What does the Contact being closed signify?

52F1-MOC I know 52F1 is a breaker, What is the Contact, MOC?
MOC is not listed in the Abbreviations Legend on the first sheet.
- What does the Contact being open signify?
- What does the Contact being closed signify?

86G Generator Lockout Relay. See Page 10, 7) of the Sequence Of Operation
- What does the Contact being open signify?
- What does the Contact being closed signify?

STS is not listed in the Abbreviations Legend on the first sheet.
- What does the Contact being open signify?
- What does the Contact being closed signify?

What does Float Switch LFDTS, Measure.

86U Utility Lockout Relay.
- What does the Contact being open signify?
- What does the Contact being closed signify?

49-1 is not listed in the Abbreviations Legend on the first sheet.
- What does the Contact being open signify?
- What does the Contact being closed signify?

OLRT is not listed in the Abbreviations Legend on the first sheet.
- What does the Contact being open signify?
- What does the Contact being closed signify?

LSBPS is a bypass switch, but is not listed in the Abbreviations Legend on the first sheet.
- What does the Contact being open “N” signify?
- What does the Contact being closed “BP” signify?

Looking at the Outputs for the existing GE PLC on Drawing Number E1554P-17
What is the difference between PCFR & RR.

### Further Questions:

Which Output Turns on the Generator? RR
The are two Relays RR (Generator Run Relay) &  CDR (Generator Cool Down Relay)
When it is time to Cool Down, Does RR stay on with CDR or must RR go off when CDR goes on?

Also, it says in the Description of Operation, the Cool Down Time is not controlled by the PLC, but
the Caterpillar controls. If this is true, exactly how does the PLC work with the Cool Down?

# Sequence Of Operation Notes:
## Setup
Page 10, 7)
Generator Lockout Relay 86G. Tripped by a problem. Trips Generator Breaker. Must be Manually Reset. Generator Circuit Breaker Tripped Alarm
Page 10, 8)
Load Shed Control Bypass Switch. When in Normal, Load shed is active
When device 43 is in Remote position, feeder Breakers can be controlled by future remote SADA system.
Page 10, 9)
Utility Lockout Relay 86U.Tripped by a problem. Trips Utility Breaker. Must be Manually Reset. Utility Circuit Breaker Tripped Alarm.
Page 10, 10) A blown 24VDC fuse will cause engine shutdown and show at Status Panel. After fuse is replaced, Engine control switch, ES, must be placed to the Stop/Reset Position.
## Generator Control Setup
Place ES to Auto
Place ES to Test/Offline to Run Engine manually.
Place ES to Off-CoolDown to allow Engine to cool down and then stop.
Place ES to Stop/Reset to stop Engine timmediately.

## Operation
Page 11, 1) ES
Auto = Normal unattended operation
Test / Offline = Run Engine Manually
Off-Cooldown, after Test / Offline = Allow Engine to Cool down & Then Stop.
Page 11, 2)
ECM = Engine Control Module On Caterpillar Engine
ECS = Engine Control Switch on ECM. If not in Auto, “Engine Control Not In Auto” Alarm.
## Sequence
SYS_GeneratorFault
- IB_PCRM_ECMF
- IB_PCRM_LOPAS
- IB_PCRM_HWTAS
- IB_RBA1_OSS
- IB_RBA1_OCS
SYS_GeneratorWarning
- IB_LFDTS Low Fuel
- IB_PCRM_HWTAS
- IB_PCRM_LWTAS
- IB_PCRM_LOPAS
- IB_49-1
- B_49-2
AS_GenReadyAuto1
- IB_ES_AUTO Or IB_ES_TEST_OFFLINE
- IB_86U
- IB_86G
- IB_PCRM_ECNIA Off
- IB_CS-G
AS_GenReadyForAuto (TOF)
- AS_GenReadyAuto1
- SYS_GeneratorFault Off
- ISYS_GeneratorWarning Off
AS_UtiityOff_TD / TP, DE_UtiityOffTime, LT_UtilityOffTimer Wait to Turn On Generator (.5→6Sec) 27U Off.
AS_UtiityBackOn_TD / TP, DE_UtiityBackOnTime , LT_UtiityBackOnTimer Wait to Go Back to Utility (1-30Min) 27U On.
AS_UtilityOff_Latch
AS_STS_SwitchLatch
AS_TOL_SwitchLatch
AS_ExerciseLatch
SYS_RunGenerator
AS_StopGenNormally
AS_GeneratorProblem..Generator Has a Problem, Take Offline
AS_NextStep

AS_GeneratorAtFreq
AS_GenXfer_TP, _TD, DE_GenXferTime, LT_GenWaitXfer Wait to Trip Utility Brkr.
AS_TripUtilityBreaker
AS_TriipFeeders_TD, _CV
AS_TripFeeder1
- AS_TripFeeder2
- AS_TripFeeder3
- AS_TripFeeder5
- AS_TripFeeder6
- AS_TripFeeder7
- AS_TripFeeder8
- AS_TripFeeder9
AS_FeedersTriped

AS_CloseGenBreaker
AS_GeneratorOnline
AS_CloseFeeders (Uses Routine: CloseFeeders)
- AS_CloseFeeder1
- AS_CloseFeeder2
- AS_CloseFeeder3
- AS_CloseFeeder5
- AS_CloseFeeder6
- AS_CloseFeeder7
- AS_CloseFeeder8
- AS_CloseFeeder9

AS_ShedFeedersStart_TD, AS_ShedFeeders, (Uses Routine: ShedFeeders)
- AS_ShedFeeder1
- AS_ShedFeeder2
- AS_ShedFeeder3
- AS_ShedFeeder5
- AS_ShedFeeder6
- AS_ShedFeeder7
- AS_ShedFeeder8
- AS_ShedFeeder9

End of Bring Generator Online.
Start of Take Generator Offline

AS_TripGenBreaker
AS_GeneratorStopCool
AS_GeneratorStopCool_TP._TD, DE_GeneratorStopCoolTime, LT_GenCoolTimer

AS_CloseUtilityBreaker_TP, DE_CloseUtilityBreakerTime , LT_CloseUtilityBreakerTimer
AS_CloseAllFeeders_CV, _TD
- AS_CloseAllFeeder1
- AS_CloseAllFeeder2
- AS_CloseAllFeeder3
- AS_CloseAllFeeder5
- AS_CloseAllFeeder6
- AS_CloseAllFeeder7
- AS_CloseAllFeeder8
- AS_CloseAllFeeder9
AS_FeedersClosed

## Non Sequence System
Sys_Exercise_TMR	No Load Exercise Timer (3 → 30 Days)
Sys_ExerciseDur_TMR	No Load Exercise Duration Timer (3Min → 3 Hours)
Sys_FeederBrkrsPriority (1-7) Priority of closing, 1 = highest, 8=Lowest , 0=Do Not Close. (Feeder #4 Never Opens.)
Sys_FeederBrkrs_TMR(1-7) Delay to Close When Priority Enabled.(2-30Sec)
PB_ShedReset
DE_Password, PW_Operators, PW_Engineers (Engineers Change Priorities)

# Message Display MSG_Main
- 0 Emergency Stop Pushed
- 1 Utility Lockout Relay 86U.Tripped. Reset Manually.
- 2 Generator Lockout Relay 86G. Tripped. Reset Manually & Momentarily Place the Engine Switch to STOP/RESET.
- 3 Alarm, see Alarm Banner or Alarm List.
- 10 In Manual Mode, Turn Off STS or Test Offline Switch
- 4 Generator is not In Auto.
- 5 Generator is not Ready.
- 6 Generator in Test Mode.
- 7 Generator is Ready For Auto.
- 8 Utility Power off, and Generator is going Online.
- 9 Utility Power off, and Generator is Online.
# Alarms
## Annunciator Alarms Set OB_PM1 to Annunciator
OB_Tag / IB_Tag	Description	Action	HMI Alarm
OB_SPG-12 / IB_PCRM_ECMF	ECM Fault	SYS_GeneratorFault / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-2 / IB_PCRM_ESD	Engine Shutdown	Nothing	N
OB_SPG-3 / IB_PCRM_LOPAS	Low Oil Pressure, Pre-Alarm	SYS_GeneratorWarning / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-4 / IB_PCRM_HWTAS	High Water Temperature, Pre-Alarm	SYS_GeneratorWarning / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-5 / IB_PCRM_LWTAS	Low Water Temperature, Pre-Alarm	SYS_GeneratorWarning / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-6 / IB_RBA1_OCS	Over Crank Shutdown	SYS_GeneratorFault / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-23 / IB_ES_AUTO	Engine Controls Not In Auto	Knock Down ..AS_GenReadyForAuto	N
OB_SPG-8 / IB_RBA1_LOPS	Low Oil Pressure Shutdown	SYS_GeneratorFault / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-9 / IB_RBA1_HWTS	High Water Temperature Shutdown	SYS_GeneratorFault / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-7 / IB_RBA1_OSS	Over Speed Shutdown	SYS_GeneratorFault / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-15 / IB_86U	Utility Breaker Tripped 86U	Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-10 / IB_86G	Generator Breaker Tripped 86G	Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-24 / IB_PCRM_ECNIA	Switch Gear Controls Not in Auto	Knock Down ..AS_GenReadyForAuto	N
OB_SPG-11 / IB_ESPB	Remote Emergency Stop Shutdown	SYS_GeneratorFault / Knock Down ..AS_GenReadyForAuto	Y
OB_SPG-21 / IB_STS	System Load Test On	Nothing	N
IOB_SPG-22 / IB_ES_TEST_OFFLINE	No-Load Test Mode On	Nothing	N
IOB_SPG-16 / IB_LFDTS	Low Fuel Day Tank Alarm	SYS_GeneratorWarning / Knock Down ..AS_GenReadyForAuto	Y
IOB_SPG-20 / IB_27U	Utility Power Failure	Nothing	N
IOB_SPG-13 / IB_49-1	High Stater Temperature, Pre-Alarm	SYS_GeneratorWarning / Knock Down ..AS_GenReadyForAuto	Y
IOB_SPG-18 / IB_49-2	High Stater Temperature, Shutdown	SYS_GeneratorFault / Knock Down ..AS_GenReadyForAuto	Y
IOB_SPG-14 / IB_UFM	Buss Overload	Nothing	N

## HMI Alarms
OB_Tag / IB_Tag	Description	Action
ALM_52F1_Trip / ALM_52F1_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close
ALM_52F2_Trip / ALM_52F2_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52F3_Trip / ALM_52F3_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52F5_Trip / ALM_52F5_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52F6_Trip / ALM_52F6_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52F7_Trip / ALM_52F7_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52F8_Trip / ALM_52F8_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52F9_Trip / ALM_52F9_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52G_Trip / ALM_52G_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing
ALM_52U_Trip / ALM_52U_Close	Feeder Breaker Failed to Trip / Feeder Breaker Failed to Close	Nothing

# Parts List
1- EA9-T15CL-R (screen)
1- P3-550E (CPU)
1- P3-08B (Base)
1- P3-01AC (Power supply)
3- P3-16ND3 (24vdc inputs)
3- P3-16TR (Relay outputs
2- P3-FILL (Blank fillers)
3- P3-RTB (Terminal blocks)