# Information for Rick

P2-16TA, AC Output Module, 16 Points. 0.5A per Output, 4.0 A per Common.

# Hopper Full Sensors

FS_H1T1F	Full Sensor, Hopper 1 from Truck 1 Full
FS_H1T2F	Full Sensor, Hopper 1 from Truck 2 Full
FS_H2T1F	Full Sensor, Hopper 2 from Truck 1 Full
FS_H2T2F	Full Sensor, Hopper 2 from Truck 2 Full

# IO From Rick

# General Information:
## Phase 1
Number of Motors: MCC1
VFD’s	27
Soft Starts	44
Total	71

VFD 1, 2, 4, 5 ,6, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22,
26, 27, 28, 29, 30, 31, 70 =27

Number of Motors: MCC2
VFD’s	6	Non Ethernet 83, 84, 85, 86, 87, 88
Soft Starts	11
Total	17

## Phase 2
Number of Motors
VFD’s	9
Soft Starts	20
Total	29

## Phase 3
Number of Motors
VFD’s	6
Soft Starts	12
Total	18

# Modbus Addressing:
## Coils
000001->000199	M01_Running -> M199_Running, VFD1->VFD200_Running
000201->000399	M01_TB -> M199_TB
000401->000599	M01_MOL > M199_MOL, VFD1->VFD200_FaultAlm
000601->000699	VFD01→VFD199_CommAlm
000801->000999	VFD01->VFD199_WarnAlm
001001->001099	Misc. Alarms
001101->001199	Misc. PB, LT & Inputs
## Int
VFD01_SPEED to VFD199_SPEED	0→100%	400001- 400199

# Motor & VFD Tags:
## FVNR Starters & Soft Starts
Tag	Modbus Address
MXX_Run (Run Motor)
MXX_Running (Motor is Running)	000001->000199
MXX_TB (Manual Mode Toggle Button)	000201->000399
MXX_MOL(Motor Overload Alarm)	000401->000599
MXX_Run_TOD (Run Motor On Delay Timer Done)

## VFD’s
Tag	Modbus Address
MXX_Faulted
MXX_Warning
MXX_RunningForward
MXX_RunningReverse
MXX_Ready
MXX_Running (Motor is Running + Off Delay)	000001->000199
MXX_TB (Manual Mode Toggle Button)	000201->000399
MXX_FaultAlm (VFD Fault Alarm)	000401->000599
MXX_ComAlm (VFD Communications Alarm)	000601->000799
MXX_WarnAlm (VFD Warning Alarm)	000801→000999
MXX_SPEED (Int, 0→100%)	400001- 400199
MXX_Run (Run Motor)
MXX_Run_TOD (Run Motor On Delay Timer Done)
MXX_VFDRunnng (Motor VFD Running )
MXX_Reset_TFD (Fault Reset Off Delay Timer Done)
MXX_Reset_FLSR (Fault Reset Flasher)
MXX_FltAlm_TOD (Fault Alarm On Delay Timer Done)

# IP Addresses:
Device	IP Address	Device Type
Motor VFD	192.168.110.(Motor # 1->199)	Eaton PowerXL DG1
Huller PLC #1	192.168.110.201	Productivity 2000
Huller PLC #2	192.168.110.202	Productivity 1000
Drier PLC #3	192.168.110.203	Productivity 2000
Huller HMI #1	192.168.110.221	Cmore EA9-T15CL
Huller Remote HMI #2	192.168.110.222	Cmore EA9-T15CL
Drier HMI #3	192.168.110.223	Cmore EA9-T15CL
Drier Remote HMI #4	192.168.110.224	Cmore EA9-T15CL
Programming PC	192.168.110.240	IBM PC

# Eaton PowerXL DG1 VFD

Ethernet/IP

EDS File imported PowerXL DG1

## Commissioning VFD With Keypad.

Connect Real Time Clock Backup Battery Connector.

Start up Wizzard: