# Automatic Sequence
AS_LowPressClose
AS_LowPressClose_T
AutoSeqStarted
AS_HighPressClose
AS_HPC_Close_Vx_T
AS_HPC_Open_V1_T
AS_FeedFilter
AS_FeedFilter_T <-- DE_FeedFilter
AS_FF_WeightOK
AS_LowFeedWeight
AS_LowFeedAck
AS_ResetFF
AS_FF_Repeat
AS_MembComp_Ena
AS_MembComp
AS_MembComp_T <-- DE_MembComp
AS_AirDry
AS_AirDry_T <-- DE_AirDry
AS_TopBlowAir1
AS_TopBlowAir1_T <--DE_TopBlow2Air1
AS_TopBlowWat
AS_TopBlowWat_T<-- DE_TopBlow2Water
AS_TopBlowAir2
AS_TopBlowAir2_T <--DE_TopBlow2Air2
AS_Drain
AS_Drain_T <-- DE_Drain
MAS_OpenHatch
MAS_OpenLowerHatch_T
MAS_HatchesOpen_T
MAS_OpenPress
AS_VibrateCloth
AS_VibrateCloth_T <-- DE_ClothVibrate
AS_EmptyWeightIsHigh
AS_HighEmptyWeight
AS_HighEmptyAck
MAS_CloseHatch
MAS_CloseUpperHatch_T
MAS_HatchesClosed_T
AS_ClothFlush
AS_ClothFlush_T <-- DE_ClothWash
AS_ClothVibWash
AS_ClothVibWash_T <-- DE_ClothVibWash
AS_Done
AS_Wait
AS_Wait_T <-- DE_DelayedStart

# HMI Notes
Buttons cannot be made invisible.
Buttons connot be disabled
Goto Buttons Cannot show a disabled state, cannot use Goto Button, must set bit in PLC
Buttons: Raised, Solid, Rectangle
Border uses Back Color & Width = 2
Button Color Select Other and second from right at bottom
Arial 10

# Main Screen Graphics & Pipes
Pipe 1	Good Air, Aqua.
Pipe 1
Pipe 2
Pipe 3
Pipe 5
Pipe 4
Pipe 6
Pipe 7
Pipe 8
Pipe 9
Pipe 10
Water
Pipe #	Condition 1	Condition 2	Condition 3	Condition 3
1 & Tag	Good Air = Aqua	Bad Air = Gray
2	V 7 Open = Aqua	Else = Green
3	V 5 Open = Aqua	Else = Green
4	V 9 Open = Blue	Else = Gray
5	V 6 Open = Aqua	V 8 Open = Blue	Else = Gray
6	Air Drying = Gray	Else = Green
7	V3 Open = Green	Else = Gray
8	V1 Open & V4 Closed = Brown	V4, V7, V6 Open = Aqua	V4, V7, V8 Open = Blue	Else = Gray
9 & Tag	V1 & V4 Open = Brown, Brown	V4, V7, V6 Open = Aqua & Brown	V4, V7, V8 Open = Blue & Brown	Else = Gray & White
Water	Good Water = Blue	Else = Gray
10 Tag, / Pipe Always Lt Brown	V1 Open = Lt Brown	Else = White

# Alarms Word 1
Alarm Discription	Alarm Address
Drying Air Not OK	ALM_W1.0
Slurry System Not OK	.1
Wash Water System Not OK	.2
High Pressure Pump Motor Overload	.3
Low Pressure Pump Motor Overload	.4
Slurry Valve, V1, Failed to Open	.5
Slurry Valve, V1, Failed to Close	.6
Spare Valve, V2, Failed to Open	.7
Spare Valve, V2, Failed to Close	.8
Filtrate Valve, V3, Failed to Open	.9
Filtrate Valve, V3, Failed to Close	.10
Slurry Return Valve, V4, Failed to Open	.11
Slurry Return Valve, V4, Failed to Close	.12
Drying Air Valve, V5, Failed to Open	.13
Drying Air Valve, V5, Failed to Close	.14
Top Blow Air Valve, V6, Failed to Open	.15
Top Blow Air Valve, V6, Failed to Close	.16
Membrane Air Valve, V7, Failed to Open	.17
Membrane Air Valve, V7, Failed to Close	.18
Top Blow Water Valve, V8, Failed to Open	.19
Top Blow Water Valve, V8, Failed to Close	.20
Wash Water Valve, V9, Failed to Open	.21
Wash Water Valve, V9, Failed to Close	.22
Membrane Drain Valve, V10, Failed to Open	.23
Membrane Drain Valve, V10, Failed to Close	.24
Upper Hatch Failed to Raise	.25
Upper Hatch Failed to Lower	.26
Lower Hatch Failed to Raise	.27
Lower Hatch Failed to Lower	.28
Press Failed to Go to Neutral Position	.29
Press Failed to Go to Park Position	.30
Press Failed to Go to Press Position	.31

# Alarms Word 2
Alarm Discription	Alarm Address
Press Weight Sensor Out Of Range	ALM_W2.0
Press Pressure Sensor Out Of Range	.1
Cloth Damaged	.2
	.3
	.4
	.5
	.6
	.7
	.8
	.9
	.10
	.11
	.12
	.13
	.14
	.15
	.16
	.17
	.18
	.19
	.20
	.21
	.22
	.23
	.24
	.25
	.26
	.27
	.28
	.29
	.30
	.31